# PSK-12 Lubrication and Bearing Inspection Log

Inspection round: May 2026 planned outage.

Scope: lubrication checks, seal leakage readings, bearing housing observations, and inspection notes for installed process pump skid equipment.

# Lubrication Quantity Records

| Asset tag | Service date | Component | Item description | Unit | Value | Technician | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| P-1201A | 2026-05-06 | DE bearing | oil fill volume | L | 1.25 | MT-AR | Filled to upper sight mark after drain |
| P-1201B | 2026-05-06 | DE bearing | oil fill volume | L | 1.20 | MT-AR | Sight glass centerline |
| P-1201C | 2026-05-07 | DE bearing | oil fill volume | L | 1.20 | MT-JP | Sight glass centerline |
| P-1202A | 2026-05-08 | DE bearing | grease quantity added | g | 28 | MT-JP | Two full pump strokes |
| P-1202B | 2026-05-08 | NDE bearing | grease quantity added | g | 31 | MT-AR | Purge visible at lower drain |
| P-1210A | 2026-05-09 | DE bearing | oil fill volume | L | 1.05 | MT-SL | Correct to mid sight glass |
| P-1210B | 2026-05-09 | DE bearing | grease quantity added | g | 34 | MT-SL | Purge visible |
| P-1220A | 2026-05-10 | DE bearing | grease quantity added | g |  | MT-AR | Grease gun counter failed during round |

# Bearing and Seal Inspection Records

| Asset tag | Service date | Component | Item description | Unit | Value | Condition | Inspector | Comment |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| P-1201A | 2026-05-06 | Mechanical seal | seal leakage | ml/min | 6 | A | MT-AR | Stable drip from quench outlet |
| P-1201B | 2026-05-06 | Mechanical seal | seal leakage | ml/min | 12 | B | MT-AR | Catch bottle reading after ten minutes |
| P-1201C | 2026-05-07 | DE bearing | bearing temperature | degC | 81 | C | MT-JP | Thermal image tag TT-1201C attached |
| P-1202A | 2026-05-08 | Motor foot | soft foot front left | mm | 0.05 | B | MT-JP | Repeat reading after loosen-tighten cycle |
| P-1202B | 2026-05-08 | NDE bearing | vibration velocity vertical | mm/s | 4.2 | B | MT-AR | Copied from VM-44 route |
| P-1210A | 2026-05-09 | Coupling | axial gap | mm | 3.2 | A | MT-SL | Spacer gap from feeler gauge |
| P-1210B | 2026-05-09 | Mechanical seal | seal leakage | ml/min | 3 | A | MT-SL | No steady stream |
| P-1220A | 2026-05-10 | Mechanical seal | seal leakage | ml/min | 5 | B | MT-AR | Intermittent weep observed |

# Part Number Cross-Check Notes

| Asset tag | Component | Item description | Unit | Value | Record source | Note |
| --- | --- | --- | --- | --- | --- | --- |
| P-1201A | DE bearing | bearing part number | part | 6311-C3 | removed bearing sleeve | Box label legible |
| P-1201B | Mechanical seal | seal kit part number | part | SEAL-APV-35 | seal housing tag | Tag wire intact |
| P-1202A | DE bearing | bearing part number | part | 6308-2RS | removed bearing sleeve | Box label damp but readable |
| P-1210B | DE bearing | bearing part number | part | 6310-C3 | spares issue label | Label differs from old handwritten tag |
| P-1220A | Mechanical seal | seal kit part number | part |  | seal box | Box label missing |