# PSK-12 Permit Lockout and Shift Handover Notes

Maintenance window: 2026-05-05 to 2026-05-14. Records below are copied from shift handover boards and permit packs.

# Permit and Isolation Register

| Asset tag | Service date | Permit type | Permit reference | Lockout reference | Verifier | Component | Item description | Note |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| P-1201A | 2026-05-06 | mechanical isolation | MI-1201A-06 | LOTO-PSK12-001 | OP-CR | Coupling guard | guard removal permit | closed after guard refitted |
| P-1201B | 2026-05-06 | mechanical isolation | MI-1201B-06 | LOTO-PSK12-002 | OP-CR | Mechanical seal | seal inspection permit | closed |
| P-1201C | 2026-05-07 | mechanical isolation | MI-1201C-07 | LOTO-PSK12-003 |  | DE bearing | temperature check isolation | verifier initials not recorded |
| P-1202A | 2026-05-08 | mechanical isolation | MI-1202A-08 | LOTO-PSK12-004 | OP-JS | Motor foot | soft foot check | closed |
| P-1202B | 2026-05-08 | hot work |  | LOTO-PSK12-005 | OP-JS | Baseplate | paint touch-up near drain channel | permit reference blank on handover sheet |
| P-1210A | 2026-05-09 | confined access | CA-1210A-09 | LOTO-PSK12-006 | OP-MN | Coupling | coupling spacer measurement | closed |
| P-1210B | 2026-05-09 | mechanical isolation | MI-1210B-09 | LOTO-PSK12-007 | OP-MN | Bearing housing | grease purge check | closed |
| P-1220A | 2026-05-10 | chemical line break | CLB-1220A-10 | LOTO-PSK12-008 | OP-VT | Mechanical seal | quench line inspection | closed |

# Shift Handover Notes

| Shift | Asset tag | Service date | Component | Item description | Unit | Value | Handover note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| night | P-1201A | 2026-05-06 | Coupling | horizontal offset | mm | 0.13 | night shift reading before final motor move |
| day | P-1201B | 2026-05-06 | Mechanical seal | seal leakage | ml/min | 13 | catch bottle emptied at start of shift |
| day | P-1201C | 2026-05-07 | DE bearing | bearing temperature | degC | 82 | recheck requested next start |
| night | P-1202B | 2026-05-08 | NDE bearing | vibration velocity vertical | mm/s | 4.2 | value copied from vibration route |
| day | P-1210A | 2026-05-09 | Coupling | axial gap | mm | 3.3 | gap checked after coupling cover installed |
| night | P-1220A | 2026-05-10 | Mechanical seal | seal leakage | ml/min |  | quench line stain seen but no measured leak value |

# Record Handling Notes

Rows with blank permit references or blank measured values should remain unresolved in record reconciliation.

Handover comments are operational records and are not return-to-service approvals.